## Slide 1: Case Study: Bench Scale Testing to Identify Lead and Copper Treatment Technique for LCR Compliance
2018 RCAP Conference
April 25, 2018

## Slide 2: “The fundamental obstacle to creating community sustainability and implementing an effective strategy is capacity; a lack of time, resources, knowledge, and staff.”
Nathan Ohle
Executive Director RCAP
Notes: This is a story of one tribal system that at one time or another faced all these obstacles, but overcame or compensated for most in dealing with lead challenges except very specialized knowledge. As technical assistance providers RCAC assisted the Tribe in securing the necessary knowledge to bring the system into compliance.

## Slide 3: Location
Big Valley Rancheria - Lake County, CA
Tribe: Big Valley Band of Pomo Indians of the Big Valley Rancheria
Serves:
  38 Residences
  Konocti Vista Casino
  Motel
  Tribal Offices
  RV Park
  Plans: 200 more residences
Notes: The Rancheria is located approximately 80 miles northwest of Sacramento.

## Slide 4: Challenges To Be Addressed
Intermittent Lead and Copper Exceedances for 14 years
Bad Raw Water Quality
Inadequate Treatment
Sewer and Water Treatment equipment in same building
Notes: Quality Issues: High - corrosivity, iron, manganese, hardness, CO2, turbidity, color
Treatment Issues: Greensand Treatment Iron removal rate 60% causing excessive sludge in finished water tank

## Slide 5: Original Treatment Features (2003)
• Potassium Permanganate Injector
• Ozone and Air Preparation System
• Iron Filters
• Ultraviolet Light System
• Multimedia Filters
• Carbon Filters
• Water Softener
• Chlorine Injection System
• External Potable Water Holding Tank
• Grundfos Boosterpaq Pumps
• Diesel Fire Pump

## Slide 6: Original Treatment Features (2015)
• Potassium Permanganate Injector
• Ozone and Air Preparation System
• Iron Filters
• Ultraviolet Light System
• Multimedia Filters
• Carbon Filters
• Water Softener
• Chlorine Injection System
• External Potable Water Holding Tank
• Grundfos Boosterpaq Pumps
• Diesel Fire Pump

## Slide 7: Existing Water and Sewer Components
Swr Wtr Softeners Carbon Multimedia Swr Swr Pumps Chem Pumps Filters Filters Screen Pumps

## Slide 8: Lead and Copper Rule Compliance History
Three years after the plant went on line a report chronicled lead exceedances

## Slide 9: Water Quality Conditions
High corrosivity Constant
High iron Variable
High manganese Constant
High hardness (Motel softens water)
High CO2 Constant
High turbidity Periodic
High color Periodic
Taste Okay
Odor Okay

## Slide 10: Creative Process
Professional Search
EPA Collaboration
Contract Negotiation

## Slide 11: Contract
EPA Funded Investigation: $25,000
Corrosion control and quality improvement testing: Kennedy/Jenks Consultants
  Corrosivity Evaluation
  Corrosion Control Options
  Pilot Testing
  Comparison of alternatives
  Cost: Capital and Operations
  Report and Recommendations

## Slide 12: Corrosion Control Theory and Testing
Water Quality Parameter Testing
Plotting the balance/imbalance of chemical compounds at Various Points in System

## Slide 13: Corrosion Control Options
pH Elevation:
  Air stripping
  Caustic addition
Adding Corrosion Inhibitors:
  Phosphates
  Silicates
Notes:   Phosphate: Previously used 3 mg/L, 30% ortho, and 70% poly blend and other phosphate blends and dosages. Not sufficiently effective.
  Silicate: Too much silica with 80 mg/L in well water can inhibit iron and manganese removal at pH above 7.2

## Slide 14: Actual Testing
18 – Liter Capacity Tub
3.4 Liters per Minute small aquarium aerator
Notes: A small aquarium aerator was used to supply the air through several plastic tubes that were
placed in the bottom of an 18-liter capacity plastic tub which had a depth of 15 inches. The
aeration capacity was 3.4 liters per minute and two air tubes were placed in the bottom of the
filtered water that had initial pH ranges of 6.6 to 6.8.

## Slide 15: Lead and Copper LPR Probes in Tub Cover

## Slide 16: Bench Scale LPR Test Assembly Tested Each Week after Aeration CO2 Stripping

## Slide 17: Linear Polarization Testing Each Week of CO2 Stripped, pH Elevated Phosphate Inhibited Water

## Slide 18: Corrosion Rate Readout in mils/year

## Slide 19: Copper Probes – Before and After

## Slide 20: Lead Probes – Before and After

## Slide 21: Bench Scale Corrosivity Testing
Week | Existing Water |  | CO2 Stripped Water |  |  | Corrosion Reduction Percent
 | pH | Copper Corrosion Rate mils/yr | pH | Copper Corrosion MPY | Lead Rate MPY | 
0 | 6.9 | - | 8.2 | - | - | -
1 | 6.9 | 8.02 | 8.2 | 2.2 | 2.1 | -
2 | 6.7 | 0.69 | 8.3 | 0.18 | 0.16 | 73
3 | 7.5 | 0.88 | 8.0 | 0.23 | 0.14 | 74
4 | 7.5 | 0.76 | 8.0 | 0.14 | 0.11 | 83

## Slide 22: Recommended Interim Water Treatment Improvements
Interim:
  Diffused air stripper: 60-minute detention at 130 GPM
  Improved iron and manganese removal: Pyrolusite media to three existing and conversion of two GAC and four Zeolite filters to pyrolusite to reduce loading rate by two-thirds.
Notes: The apparent best alternative for a relatively low cost interim treatment to reduce the corrosivity of the water is to provide air stripping of CO2 with about an hour detention and concurrent pH elevation to about 8.0. An 8,000-gallon tank located near the storage tank would receive filtered and disinfected water and provide gravity flow into the storage tank. It is also desirable to improve the iron and manganese removal by retrofitting all of the GAC and zeolite pressure

## Slide 23: Recommended Interim Water Treatment Improvements - Continued
Interim:
  Storage tank: Sludge removal and cathodic protection
  Cost: $200,000 interim treatment and $300,000 wastewater treatment plant separation by containment wall ($100,000 CO2 stripping and $100,000 improved iron removal)

## Slide 24: Long Range Treatment (for wastewater separation)
CO2 Stripping
Water Softening by Lime with Iron-Manganese Precipitation
Filtration
Chlorination
Phosphate Inhibitor
Cost: $3 million
Notes: The long range solution involves the construction of a new water treatment facility that will achieve physical separation of wastewater treatment activities. The new plant will incorporate the CO2 stripping and the treatment processes will incorporate more automatic functions designed to treat the raw water quality that has been quantified by years of operation of the present plant.

## Slide 25: Project Outcome
Interim Water Treatment Improvements
  Components:
    Diffused air stripper
    Improved iron and manganese removal
    Storage tank sludge removal and cathodic protection
  Cost: $200,000 interim treatment ($300,000 with wastewater separation) to achieve:
    Projected 80% reduction in corrosion rate
    Lead and Copper Rule compliance
    Lower treatment costs (Chemicals and Labor)
  New treatment plant process improvements identified
Notes: Improved iron and manganese removal reducing loading rate by two-thirds

## Slide 26: Project Outcomes
Tribal technical and managerial capacities expanded
Confidence built in outcome
Better understanding of responsibilities

## Slide 27: RCAC Assistance
Corrosion control and quality improvement testing
RCAC provided Assistance with:
  Funding application
  Finding qualified engineering consultant
  Professional service consultant contract provisions
  Bench scale testing
  Reviewing report and recommendations

## Slide 28: Big Valley Rancheria Corrosion Control Study Lessons Learned
Find the right engineer/scientist
The importance of collaboration between involved parties
Teachable Lessons
  Obvious treatment methods aren’t
  Importance of monitoring

## Slide 29: The Collaborators
John Gicucki – Big Valley Rancheria Public Works Manager
John Cruz – Big Valley Rancheria Lead Operator
Sarah Ryan – Big Valley Rancheria Environmental Director
Jason Gambatese – EPA Region 9 Project Manager
Robert Ryder – Kennedy/Jenks Engineers

## Slide 30: Big Valley Rancheria Corrosion Control Study
For Further Information
      Lee Schegg
      lschegg@rcac.org
      916-704-8134

## Slide 31: Big Valley Rancheria Corrosion Control Study
Questions?